MW Scalability Level PV/ESS Test System Solution

# Overview

## 1.1 Introduction

The PV/ESS Testing System is a system solution provided by Actionpower for photovoltaic inverters, power conversion system (PCS), and battery modules (clusters). It is mainly used to test whether the functions and performance characteristics of photovoltaic inverters, energy storage inverters, and battery modules (clusters) meet the design and related standards requirements. The grid simulator and DC power supply have parallel expansion interfaces to meet the testing requirements of various power levels of test specimens.

Throughout the entire testing process, the system conducts procedural tests according to pre-selected test items, automatically records test data, analyzes data, and generates reports with a single click, greatly improving testing efficiency, saving time, and reducing costs for equipment manufacturers and testing agencies.

## 1.2 Solution

- The schematic diagram example (7.5MW)of the principle is as follows:

- Clarification

This area consists of one set of 6MW testing platform and one set of 1.5MW testing platform, mainly used for electrical performance testing of photovoltaic inverters, energy storage inverters, and other equipment up to 6MW, and also capable of connecting the 1.5MW system to the 6MW system to form a 7.5MW testing system for testing equipment up to 7.5MW.

The system consists of 6 workstations(7.5MW, 1.5MW, 3MW, 1.5MW, 1.5MW, 750kW), which can be flexibly paralleled to form testing systems of different capacities for testing specimens of different capacities, improving the efficiency of system operation.

The AC grid simulator in the system is mainly used to simulate various grid disturbances such as voltage deviations, frequency deviations, unbalanced three-phase voltages, voltage fluctuations and flickers, frequency fluctuations, voltage harmonics, and inter-harmonics caused by grid faults. It can also simulate various operating conditions such as voltage drops and rises caused by grid faults, used for voltage adaptability testing, frequency adaptability testing, unbalance adaptability testing, flicker adaptability testing, harmonics adaptability testing, inter-harmonics adaptability testing, high/low voltage ride-through testing, etc., meeting the grid connection testing requirements of photovoltaic inverters, energy storage inverters, etc.

The DC power supply is mainly used for P-V simulation, battery simulation, etc. It can simulate various output characteristics of photovoltaic panels, provide various customized curves, static and dynamic I-V curve simulations, and can simulate standard curves such as Sandia, EN50530, CGC/GF004, etc. It should include at least 7 common battery models such as lithium iron phosphate, ternary lithium, nickel-metal hydride, lead-acid batteries, etc., simulate the output characteristics, charge and discharge characteristics of battery packs, set parameters such as series-parallel quantity, temperature, SOC, internal resistance, single-cell battery capacity, etc.; open 1st, 2nd, 3rd order RC battery models, and customize battery parameters. In addition, it should have programming capabilities, simulate different waveforms output through Step, List, and Wave programming modes to meet other testing requirements.

# Feature

- Support for the latest standard test project requirements.

- The system meets all electrical performance testing requirements for PV inverters and energy storage inverters up to 7.5MW.

- The system can conduct charge and discharge tests for battery packs.

- The high-capacity testing area includes 6 workstations, capable of simultaneously testing 6 specimens, thereby increasing the utilization of the experimental system.

- The switchgear allows for both local and remote operation, with reliable safety interlocking functions.

- The performance of the grid simulator and battery simulator in parallel are equivalent to those of a single power supply.

- The grid simulator can simulate normal and abnormal characteristics of the grid, meeting the adaptability testing requirements of grids in various countries.

- Fully automated testing process, completing testing content with one click and exporting reports.

- All test data within the system is automatically saved, ensuring the authenticity and accessibility of the raw data.

# Test regulation

## Regulation followed

| No. | Regulation | Description |
| --- | --- | --- |
| 1 | NB/T 32004-2018 | Technical specification of PV grid-connected inverter |
| 2 | CGC/GF 035：2013 CNCA/CTS 0002-2014 | 光伏并网逆变器中国效率技术条件 |
| 3 | GB/T 19964-2012 | Technical requirements for connecting photovoltaic power station to power system |
| 4 | Q / GDW 1617-2015 | Technical requirements for connecting photovoltaic power station to power grid |
| 5 | GB/T 13422-2013 | Semiconductor converters -- Electrical test methods |
| 6 | GB/T 34120-2017 | Technical specification for power conversion system of electrochemical energy storage system |
| 7 | GB/T 34133-2017 | Testing code for power converter of electrochemical energy storage system |
| 8 | NB/T 31016-2011 | General specification for power control system of battery energy storage system |
| 9 | GB/T 33593-2017 | Technical requirements for grid connection of distributed resources |
| 10 | NB/T 33011-2014 | Technical specification for test of equipments interconnecting distributed resources with power grid |
| 11 | NB/T 32015-2013 | Technical rule for distributed resources connected to distribution network |
| 12 | Q/GDW 666-2011 | Technology Specification for Testing of Connecting Distribution Generation into Distribution Network |
| 13 | GB/T 33589-2017 | Technical requirements for connecting micro-grid to power system |
| 14 | GB/T 34129-2017 | Specification for test of micro-grid connected to distribution network |
| 15 | GB/T 36547-2018 | Technical rule for electrochemical energy storage system connected to power grid |
| 16 | GB/T 36548-2018 | Test specification for electrochemical energy storage system connected to power grid |
| 17 | NB/T 32004-2018 | Technical specification of PV grid-connected inverter |
| 18 | GB/T 34120-2017 | Technical specification for power conversion system of electrochemical energy storage system |
| 19 | GB/T 34133-2017 | Testing code for power converter of electrochemical energy storage system |
| 20 | GB/T 36547-2018 | Technical rule for electrochemical energy storage system connected to power grid |
| 21 | GB/T 36548-2018 | Test specification for electrochemical energy storage system connected to power grid |
| 22 | GBT 36276-2018 | Lithium ion battery for electrical energy storage |
| 23 | NB/T 31016-2011 | General specification for power control system of battery energy storage system |
| 24 | VDE-AR-N 4105:2017 | Generators connected to the low-voltage distribution network - Technical requirements for the connection to and parallel operation with low-voltage distribution networks |
| 25 | BDEW Technical Guideline: 2008 | Technical Guideline Generating Plants Connected to the Medium-Voltage Network |
| 26 | CEI 0-21: 2016 | Technical rules for Low Voltage (LV) connections of active and passive users to Utilities of electrical energy |
| 27 | CEI 0-16: 2016 | Reference technical rules for the connection of active and passive consumers to the HV and MV electrical networks of distribution company |
| 28 | UL1741SA | Standard for Inverters, Converters, Controllers and Interconnection System Equipment for Use With Distributed Energy Resources |
| 29 | GB/T 37408-2019 | Technical requirements for photovoltaic gird-connected inverter |
| 30 | EN 50530-2010 | Overall efficiency of grid connected photovoltaic inverters |
| 31 | VDE-AR-N 4105:2017 | Generators connected to the low-voltage distribution network – Technical requirements for the connection to and parallel operation with low-voltage distribution networks |
| 32 | BDEW Technical Guideline: 2008 | Technical Guideline Generating Plants Connected to the Medium-Voltage Network |
| 33 | UL 1741-1999(R2016) | Standard for inverters, converters, controllers and interconnection system equipment for use with distributed energy resources |
| 34 | CEI 0-21: 2016 | Technical rules for Low Voltage (LV) connections of active and passive users to Utilities of electrical energy |
| 35 | CEI 0-16: 2016 | Reference technical rules for the connection of active and passive consumers to the HV and MV electrical networks of distribution company |
| 36 | Grid-interconnection code JEAC 9701-2012 | Measures for facilities required for grid interconnection |
| 37 | IEC TS 62910:2015 | Utility-interconnected photovoltaic inverters – Test procedure for low voltage ride-through measurements |
| 38 | IEEE 1547 | Standards Coordinating Committee 21(Fuel Cells, Photovoltaic ,Dispersed Generation,and Energy Storage) |
| 39 | IEC 61000-3-15 | Limits-Assessment of low frequency electromagnetic immunity and emission requirements for dispersed generation systems in LV network |
| 40 | IEC 62116 Ed.2 (2014) | Utility-interconnected photovoltaic inverters – Test procedure of islanding prevention measures |
| 41 | DIN-VDE0126-1-1 | Automatic disconnection device between a generator and a public low voltage |
| 42 | CGC/GF004TM.1:2012 | 并网光伏发电专用逆变器试验方法 第1部分：电性能 |
| 43 | IEC61000-4-7 | Testing and measurement techniques - General guide on harmonics and interharmonics measurements and instrumentation,for power supply systems and equipment connected thereto |
| 44 | IEC61000-3-12 | Limits -Limits for harmonic currents produced by equipment connected to public low-voltage systems with input current 16 A and 75 A per phase |
| 45 | GB/T 12325-2008 | Power quality -- Deviation of supply voltage |
| 46 | GB/T 12326-2008 | Power quality -- Voltage fluctuation and flicker |
| 47 | GB/T 14549-1993 | Quality of electric energy supply. Harmonics in public supply network |
| 48 | GB/T 15543-2008 | Power quality -- Three-phase voltage unbalance |
| 49 | GB/T 15945-2008 | Power quality -- Frequency deviation for power system |

## Test items followed

| Electrical performance test capacities of PV/ESS |  |  |  |
| --- | --- | --- | --- |
| MPPT efficiency test | Fault ride-through | Grid voltage adaptability detection | Overload detection |
| conversion efficiency | Anti-island performance detection | Grid frequency adaptability detection | Voltage deviation |
| THD | Current interharmonic detection | Interharmonic adaptability | Flicker adaptation |
| Unbalanced 3-phase detection | Current harmonic detection | Power factor detection | Voltage sag, interruption, fluctuation |
| Active power detection | Reactive power detection | DC component detection | Flicker detection |
| Charge and discharge conversion time detection | Current error detection | Current accuracy detection on CC mode | Current ripple coefficient detection on CC mode |
| Voltage error detection | Voltage accuracy detection on CV mode | Voltage ripple coefficient detection on CV mode | Grid Interconnection/Disconnection Switching Time Measurement |
| Efficiency detection | Output frequency deviation detection | Voltage harmonic detection | Output voltage deviation detection |
| Voltage interharmonic detection | Voltage transient value detection | Low/High temperature operating test | Humidity range test |
| Insulation |  |  |  |
| Battery pack charging and discharging test content |  |  |  |
| Capacity and Energy Testing | Energy efficiency test | Over-temperature protection | Overcharge protection |
| High/low temperature start | Room temperature capacity and energy | Room temperature power | Standard cycle life |
| Overdischarge protection |  |  |  |

## Support for future upgrades

The system support to add battery charging and discharging functions. Battery charge-discharge testing system is a comprehensive testing system designed for the comprehensive performance testing of power battery packs in accordance with industry-related standards requirements.

# Software

## 4.1 Overview

Action 2020 Industry Solution Integrated development environment, applicable to various industries: manufacturer R&D testing, system integration, production line automated testing, testing agency verification testing, etc.

Providing virtual control panels for equipment, visually displaying the operation status of each device.

## 4.2 Feature

| - Device management | - Support for ATE integrated equipment registration - Ability to add, delete, and publish various types of devices - Equipped with one-click device diagnosis function - Ability to set source-load type of combinations - Support for hardware configuration import and export - Ability to perform system hardware replication |
| --- | --- |
| - Test case services | - Drag-and-drop for complex test item editing - Compilation checks for test case - Highlighting of compilation and simulation errors - Support for importing and exporting test items via Excel |
| - Test program services | - Integration of standards, product testing, and inspections through test case combination - Support for compliance checks - Highlighting of compilation and simulation errors - Support for importing and exporting test items via Excel |
| - Solution services | - One-click to start testing - Highlighted execution items - Quick display of PASS/FAIL results - Automatic adaptation of EUT parameters |
| - Test report service | - Customization of report style and content - Support for importing Word templates - Automatically adapting template to fill in test data and generate reports |
| - Statistical Analysis Services | - Test data analysis and statistics - Built-in selection of statistical rules - Daily, monthly, yearly reports - Reserved MES push interface |
| - Multi-user login | - To meet the software permission management requirements of customers, different interface levels are set up for testing, R&D, production line, and other positions, including operator, programmer, and administrator levels, providing more flexible operation and easier management. |
| - User-friendly operation | - User-friendly operating interface, making operations easy and the interface friendly. During testing, the status of running steps is clearly visible, with real-time display of current and voltage curves. The testing process data is very intuitive, and specific values can be viewed through the data box. - Test waveform can be exported as image files, making it convenient for writing test reports and other purposes. - It supports multi-channel display, requiring only one workstation to control the operation of multiple devices, allowing real-time monitoring of data from each device. |
| - Multiple editing | - Three editing interfaces are provided, namely CAN Data, MODBUS Data, and Step Management. - For CAN Data, it supports direct import of dbc files into CAN data files, and allows for content editing. Different CAN data files can be configured for different products. - For MODBUS Data, it supports functional expansion. By editing or importing MODBUS data protocols, data from environmental chambers, salt spray chambers, and other equipment can be fed back to the TAS platform for real-time monitoring and control. - For Step Management, it supports up to 9999 steps, meeting the maximum requirements for complex testing processes. The diverse types of steps also provide users with different testing methods. |
| - Efficient system management | - File management, testing data path interface support querying test reports and testing data from the local database, facilitating data recording for production, maintenance, and debugging, and making it convenient for problem tracing. Additionally, it can be integrated with the factory MES system to meet customers' needs for data query and report printing anytime and anywhere. - User management can be assigned different levels of access to meet the usage requirements of various positions such as production, process, and research and development. - System settings can set system protection values, record interval times, etc., to provide a safe and convenient user experience. |
| - Customizing Reports | - At the end of system test, the test items and results will be displayed, making it convenient for users to view the test results at the end of each test without having to check local record files or records stored in the MES system. - A report will be automatically generated at the end of each test, and users can customize the format of the report. |

# Specification

The main devices list is as follows,

| Item | Feature | Parameter |
| --- | --- | --- |
| Grid simulator | Testing for grid adaptability of devices and produce stable voltage and frequency outputs, meeting relevant national standards requirements for voltage variations, frequency fluctuations, harmonics, interharmonics, imbalance, flicker, and various other power quality-related characteristics of the power supply environment. In addition to providing a power supply environment for electrical devices, grid simulator can also receive energy returned from loads and feed it back to the grid, saving energy and improving the testing environment. | - Voltage accuracy ±0.1%F.S. - Slew rate 1V/μs - 50 harmonics - 300kW ~ 1MW for single unit and scalability up to 8MW - 0 ~ 700V |
| AC Switchgear | AC Switchgear #1: The input consists of four 1.5MVA grid simulator, with an additional connection port reserved for AC switchgear #2. By toggling the switches on the switchgear, it is possible to alter the parallel operating conditions of the four grid simulator, thus varying the output capability of the power supply current. This configuration enables five different output capacities. When there is a need for larger capacity testing in the future, it is possible to connect to AC switchgear #2 and output to workstation 1, achieving a maximum output power of 7.5MW. AC Switchgear #2: The input end consists of two 750kVA grid simulator. By toggling the switches on the switchgear, it is possible to alter the parallel operating conditions of the two power sources, thus varying the output capability of the power supply current. It offers two different output capacities. | - AC Switchgear #1 - Workstation1 (1.5MW), WS2 (1.5MW), WS3 (1.5MW), WS4 (1.5MW) - WS1 (3MW), WS3 (1.5MW), WS4 (1.5MW) - WS1 (3MW), WS3 (3MW) - WS1 (4.5MW), WS4 (1.5MW) - WS1 (6MW) - AC Switchgear #2 - Workstation5 (1.5MW) - Workstation5 (750kW) Workstation6 (750kW) |
| Bidirectional DC power supply | - Constant voltage, constant current, constant power, constant resistance, programming, battery simulation, and photovoltaic standards (EN50530\Sandia) dynamic and static MPPT tracking, photovoltaic array, simulation of 7 common battery output characteristics; - Battery charge and discharge testing. | - 300kW ~ 1MW for single unit and scalability up to 8MW - 1200V&2000V - Battery simulator |
| DC Switchgear | DC Switchgear #1:The input consists of four 1.5MVA bidirectional DC power supply, with an additional connection port reserved for DC switchgear #2. By toggling the switches on the switchgear, it is possible to alter the parallel operating conditions of the four power supplies, thus varying the output capability of the power supply current. This configuration enables five different output capacities. When there is a need for larger capacity testing in the future, it is possible to connect to DC switchgear #2 and output to workstation 1, achieving a maximum output power of 7.5MW. DC Switchgear #2: The input end consists of two 750kW power supplies. By toggling the switches on the switchgear, it is possible to alter the parallel operating conditions of the two power sources, thus varying the output capability of the power supply current. It offers the two different output capacities. | - DC Switchgear #1 - Workstation1 (1.5MW), WS2 (1.5MW), WS3 (1.5MW), WS4 (1.5MW) - WS1 (3MW), WS3 (1.5MW), WS4 (1.5MW) - WS1 (3MW), WS3 (3MW) - WS1 (4.5MW), WS4 (1.5MW) - WS1 (6MW) - DC Switchgear #2 - Workstation5 (1.5MW) - Workstation5 (750kW) Workstation6 (750kW) |
| Workstation junction box | The test specimen is interfaced with the testing equipment and signal acquisition system, facilitating the connection of devices such as power analyzers, waveform recorders, etc. | Workstation1 (7.5MW) Workstation2 (1.5MW) Workstation3 (3MW) Workstation4 (1.5MW) Workstation5 (1.5MW) Workstation6 (750kW) |
| Power analyzer | Customizable |  |
| Oscilloscope | Customizable |  |